## table-3-5-tank-spacing-conditio
Type of Tank | Protection | Minimum Distance (Feet) from Property Line Which May Be Built On, Including the Opposite Side of a Public Way | Minimum Distance (Feet) from Nearest Side of Any Public Way
Floating roof | Protection for exposures* | ½ times diameter of tank but need not exceed 90' | 1/6 times diameter of tank but need not exceed 10'
| No Protection | Diameter of tank but need not exceed 175' | 1/6 times diameter of tank but need not exceed 30'
Vertical with weak roof to shell seam | Approved foam or inerting system on the tank | ½ times diameter of tank but need not exceed 90' and not less than 5' | 1/6 times diameter of tank but need not exceed 30' and not less than 5'
| Protection for exposures* | Diameter of tank but need not exceed 175' | 1/3 times diameter of tank but need not exceed 60'
| No protection | Twice diameter of tank but need not exceed 350' | 1/3 times diameter of tank but need not exceed 60'
Horizontal and vertical, with emergency relief venting to limit pressures to 2.5 psig | Approved inerting system on the tank or approved foam system on vertical tanks | ¾ times Table 3-9 but not less than 5' | ¾ times Table 3-9 but not less than 5'
| Protection for exposures* | Table 3-9 | Table 3-9
| No protection | Twice Table 3-9 | Twice Table 3-9
Caption: Table 3-5 Tank Spacing Table—Condition 1
Footnote *: Protection for exposures shall mean fire protection for structures on property adjacent to tanks. When acceptable to the authority having jurisdiction, such structures located (1) within the jurisdiction of any public fire department or (2) within or adjacent to plants having private fire brigades shall be considered as having adequate protection for exposures.
Extracted from Process-Piping-Design-Rip-Weaver-Volume-1 page 56, table 1.
Note on B2: *: Protection for exposures shall mean fire protection for structures on property adjacent to tanks. When acceptable to the authority having jurisdiction, such structures located (1) within the jurisdiction of any public fire department or (2) within or adjacent to plants having private fire brigades shall be considered as having adequate protection for exposures.
Note on B5: *: Protection for exposures shall mean fire protection for structures on property adjacent to tanks. When acceptable to the authority having jurisdiction, such structures located (1) within the jurisdiction of any public fire department or (2) within or adjacent to plants having private fire brigades shall be considered as having adequate protection for exposures.
Note on B8: *: Protection for exposures shall mean fire protection for structures on property adjacent to tanks. When acceptable to the authority having jurisdiction, such structures located (1) within the jurisdiction of any public fire department or (2) within or adjacent to plants having private fire brigades shall be considered as having adequate protection for exposures.