## tank-spacing-table-condition-3
Type of Tank | Protection | Minimum Distance (Feet) from Property Line Which May Be Built On, Including the Opposite Side of a Public Way | Minimum Distance (Feet) from Nearest Side of Any Public Way
Horizontal and vertical tanks with emergency relief venting to permit pressure not in excess of 2.5 psig | Tank protected with any one of the following: Approved water spray, Approved inerting, Approved insulation and refrigeration, Approved barricade | Table 3-9 but not less than 25' | Not less than 25'
| Protection for exposures | 2½ times, Table 3-9 but not less than 50' | Not less than 50'
| No Protection | 5 times Table 3-9 but not less than 100' | Not less than 100'
Horizontal and vertical tanks with emergency relief venting to permit pressure over 2.5 psig | Tank protected with any one of the following: Approved water spray, Approved inerting, Approved insulation and refrigeration, Approved barricade | Twice Table 3-9 but not less than 50' | Not less than 50'
| Protection for exposures | 4 times Table 3-9 but not less than 100' | Not less than 100'
| No protection | 8 times Table 3-9 but not less than 150' | Not less than 150'
Caption: Table 3-7 Tank Spacing Table—Condition 3
Extracted from Process-Piping-Design-Rip-Weaver-Volume-1 page 57, table 1.