## valve-accessibility-table
TYPE OF VALVE | TYPE OF ACCESS REQUIRED
| Grade | Fixed Platform | Rolling Platform or Scaffold | Fixed Ladder | Portable Ladder
Operating Valves (1) | Yes | Yes | No | No | No
Operating Valves, Small (1,3) | Yes | Yes | No | Yes | No
Non-operating Valves (2) | * | * | Yes | No | No
Non-operating Valves, Small (2,3) | * | * | Yes | * | Yes
Instrument Valves | (See Paragraph 5.13.1.1 - Instrument Access)
Caption: Table 1, Valve Accessibility Table
Footnote 1: Operating valves are valves that are essential for plant operation.
Footnote 2: Non-operating valves are valves that are not essential for plant operation.
Footnote 3: Small valves are defined as valves that can be easily operated with one hand and are normally NPS 2 and smaller.
Footnote *: To be used if available.
Extracted from 01-overall-piping-design-standards-02 page 24, table 1.
Note on A3: 1: Operating valves are valves that are essential for plant operation.
Note on A4: 1: Operating valves are valves that are essential for plant operation. 3: Small valves are defined as valves that can be easily operated with one hand and are normally NPS 2 and smaller.
Note on A5: 2: Non-operating valves are valves that are not essential for plant operation.
Note on B5: *: To be used if available.
Note on C5: *: To be used if available.
Note on A6: 2: Non-operating valves are valves that are not essential for plant operation. 3: Small valves are defined as valves that can be easily operated with one hand and are normally NPS 2 and smaller.
Note on B6: *: To be used if available.
Note on C6: *: To be used if available.
Note on E6: *: To be used if available.