## control-valve-bypass-clearances
VALVE | ACTUATOR | CLEARANCE
< NPS 8 | < 40 inches | 1 foot
< NPS 8 | > 40 inches | 3 feet
> NPS 8 | -- | 3 feet (915 mm) w/offset bypass. offset shall be 6 inches (150 mm) > than diameter of actuator.
Caption: Control valve by-pass clearances by valve size and actuator type
Extracted from 01-overall-piping-design-standards-02 page 50, table 1.