## table-3-instrument-access-requi
Type of Instrument | Access For Operation Required | Access From Grade And/Or
|  | Portable Required | Fixed Ladder | Fixed Platform
1. Thermocouples | No
2. Test Thermowells | Yes | Yes | ** | **
3. Dial Thermometers | No*
4. Pressure Gage | Yes | Yes | ** | **
5. Level Gages | Yes | No | Yes | **
6. Direct Mounted Temperature Transmitter, RTD's and Switches (blind/non-indicating) | No | Yes | Yes
7. Remote Mounted Transmitters and Switches | Yes | Yes | ** | **
8. Remote Mounted Transmitters and Switches (indicating) | Yes | No | Yes | **
9. Recorders and Controllers | Yes | No | No | Yes
10. Control Valves and Other Finite Control Elements | Yes | No | No | Yes
11. Pressure Relief Valves | Yes | No | No | Yes
12. Auto Samplers | Yes | No | No | Yes
13. Density / Flow Meters | Yes | No | No | Yes
Caption: Table 3, Instrument Access Requirements
Footnote *: But must be able to read from platform or fixed ladder.
Footnote **: To be used if available.
Extracted from 01-overall-piping-design-standards-02 page 75, table 1.
Note on D4: **: To be used if available.
Note on E4: **: To be used if available.
Note on B5: *: But must be able to read from platform or fixed ladder.
Note on D6: **: To be used if available.
Note on E6: **: To be used if available.
Note on E7: **: To be used if available.
Note on D9: **: To be used if available.
Note on E9: **: To be used if available.
Note on E10: **: To be used if available.