## pump-suction-discharge-pressure
| Pump Suction | Pump Discharge
Water, amine, caustic and hydrocarbon liquids more than 28°C below boiling point. | 11.3 kPA/100m (0.5 psi/100') | 22.6 kPA/100m (1 psi/100')
Water, amine, caustic and hydrocarbon liquids less than 28°C below boiling point. | 2.26 kPA/100m (0.1 psi/100') | 22.6 kPA/100m (1 psi/100')
Caption: Pump Suction and Discharge pressure drop limits
Extracted from 01-overall-piping-design-standards-03 page 5, table 1.