## bypass-valve-nominal-size-dn
MAIN VALVE, nominal size, DN | For warming-up of pipe and for pressure-balancing of pipes with limited volumes | For pressure-balancing of other pipes
150 | 20 | 40
200 | 20 | 40
250 | 25 | 40
300 | 25 | 50
350 | 25 | 50
400 | 25 | 80
450 | 25 | 80
500 | 25 | 80
600 | 25 | 100
Caption: Bypass valve nominal size, DN — for steam services valves DN 150 and larger
Extracted from 01-overall-piping-design-standards-08 page 60, table 1.