## nominal-pipe-size-distance-firs
Nominal pipe size DN | Distance between tank and first support (m)
100 and smaller | —
150 | 6
200 | 6
250 | 8
300 | 10
350 | 10
400 | 10
450 | 10
500 and larger | 12
Caption: Nominal pipe size vs. Distance between tank and first pipe support
Extracted from 01-overall-piping-design-standards-08 page 62, table 1.