## table-4-minimum-clearance-dimen
Item | Description | Dimension
Roads | Clearance over primary access roads where major maintenance vehicles are expected to pass | 5486 mm (18'-0")
| Clearance over electrical transmission and distribution lines | 6706 mm (22'-0")
| Width of primary access roads | 6096 mm (20'-0")
| Clearance over secondary access roads and pump access roads | 3048 mm (10'-0")
| Width of secondary access roads and pump access roads | 3048 mm (10'-0")
Railroads | Clearance over through-railroads (from top of rail) | 6706 mm (22'-0") (check local regulations)
| Clearance over dead ends and sidings (from top of rail) | (check local regulations)
| Horizontal clearance from track centerline to obstructions | 4877 mm (16'-0") (check local regulations)
| Clearance under electrical lines | 2591 mm (8'-6")
Check applicable regulations
Access Walkways | Clearance height for projections over platforms, working areas, walkways | 2286 mm (7'-6") 2033 mm (6'-8") (for bottom of valve handwheels)
Increased width of stairways, walkways, and landings should be considered for rescue purposes. | Width of stairways (unobstructed width) | 914 mm (3'-0")
| Width of landings (in direction of stairways) | 914 mm (3'-0")
| Width of walkways | 914 mm (3'-0")
| Maximum vertical rise of one flight of stairway | 5486 mm (18'-0")
| Maximum horizontal distance from any point on platform to an emergency exit | 22 m (75'-0")
| Maximum length of dead-end platforms | 6096 mm (20'-0")
Ladders | Maximum vertical rise of ladders in a single run | 9 m (30'-0")
| Maximum allowable slope of ladders from vertical | 15 degrees
| Minimum toe clearance from centerline of rung to obstruction | 180 mm (7")
Platforms | Maximum variance in platform elevations without an intermediate step | 305 mm (1'-0")
| Minimum unobstructed width of platforms | 762 mm (2'-6")
| Occasional obstructions (level glass, transmitter, etc.) | 457 mm (1'-6")
| Minimum width of manhole platforms on vertical vessels | 1067 mm (3'-6")
| Minimum platform extension beyond centerline of manhole flange on vertical vessels | 762 mm (2'-6")
| Minimum width of platform from three sides of manhole on vessel top-head platforms | 762 mm (2'-6")
| Minimum width of platforms at ends of horizontal tube furnaces | 1067 mm (3'-6")
Operation & Maintenance | Minimum clearance in front of channel end of horizontal exchanger for tube removal or cleaning | Tube bundle length plus 1524 mm (5 ft.)
| Minimum clearance around exchanger body flanges | 457 mm (1'-6")
| Vertical exchangers | Unobstructed vertical access
Caption: Table 4 - Minimum Clearance Dimensions
Extracted from 02-plant-layout-and-equipment-spacing-01 page 14, table 1.