## bottleneck-explanation-control-
Bottleneck | Explanation
Display Control System (DCS) | Require any of the Display Screen Equipment (DSE) to be able to bring up any of the pictures as well as normal personal computing interfaces Requires 2-man operation Due to fact that DCS is not reliable, operators are forced to monitor and operate off back wall Too many actions required to carry out simple operation Inability to handle large amounts of information
Traffic within control room | All visitors enter control room Anyone seeking signature from Shift Supervisor also enters control room - In some cases visitors 'hang around' when Shift Supervisor is not there and interact with on duty control room operators (CROs) Integration of normal personal computer (PC) screen onto DCS Information on control monitoring system (CMS) is fragmented and therefore difficult to interpret
Shift Supervisor | Needs visual and auditable contact with CROs Requires to be adjacent to PCF to sign off permits to work Because Shift Supervisor sits in same room as CROs, confidential talks are carried out in any office that can be found (not ideal for good people management); this includes discussions with visitors
Physical Environment | Lighting: - Direct lighting creates glare on DSE and cannot be controlled by operators - Lighting at Scheduler's office is poor and makeshift glare barriers have been erected. - During night shift, back wall hard-wired outputs difficult to read Thermal Environment - Variable air conditioning and poor ventilation causes CROs to constantly take off and put on jackets during the course of a shift - Complaints that the CCR is too warm in the summer and too cold in the winter Noise - Non-enclosed dot-matrix printers that provide data every 15 minutes are a distraction and add to overall background noise of the CCR
Console Layout | Mixture of controls that have been added as new systems are included in the project Safeguard that protects against inadvertent operation also covers the label for the control (therefore stickers are used to identify controls that cannot be seen) Automatic Shutdown (ASD) required to be on same panel (needs to be able to incorporate expansion) Requires that all controls are within view of operator
Scheduler | Does not need visual contact with Shift Supervisor
Caption: Bottleneck and explanation table for control room issues
Extracted from 19-project-engineering-and-documentation-02 page 42, table 1.