## table-4-1-uaw-piping-line-class
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | ERW (Type E) | ASTM A-53 GR.A T&C Galvanized | (1) (3)
| 3 to 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B or API-5L GR.B Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1) (15)
| 12 to 24 | Std. Wt. Min. | Seamless | ASTM A-53 GR.B or API-5L GR.B Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (3) (15)
| 26 and over | Calculate | Electric Fusion Welded | API-5L GR.B, TE, or BD, ASTM A-671, GR.CC60, Class 22 | (15)
FITTINGS — Ells, Tees, Reducers, etc.
| 2 & under | 2000# | Threaded | ASTM A-105, Galvanized | (1)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless Normalized | (2) (13)
Nipples & Swages
| 1 1/2 & under | See Notes | Seamless/Threaded | ASTM A106 GR.B Galvanized | (3) (4)
Threadolets
| 2 & under | 3000# | Threaded | ASTM A-105, Heat Treated | (10) (13)
Unions
| 2 & under | 3000# | Threaded | ASTM A-105 with Integral Seats, MSS SP-83 Galvanized
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (2) (10) (12) (13)
FLANGES
| 2 | 150 | WN, RF | ASTM A-105, Heat Treated | (2) (6) (10) (12) (13)
| 2 & under | 150 | Threaded, RF | ASTM A-105 | (5) (6)
| 3 & over | 150 | SO or WN, RF | ASTM A-105, Heat Treated | (2) (8) (10) (14)
BOLTING | Stud Bolts: ASTM A-193, GR.B7 with ASTM A-194, GR.2H Nuts
GASKETS | Compressed Asbestos Composition 1/16" Thick
Caption: Table 4.1 UAW Piping Line Class — Pipe, Fittings, Flanges, Bolting, Gaskets specifications
Extracted from 03-piping-materials-and-line-classes-01 page 25, table 1.