## table-4-1-class-uaw-valve-speci
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Ball
| 2 & under | 150 | Threaded | Split Bronze Body, Bronze Ball & Silicon Brass Steam, Teflon Seats and Seals, Wrench Operated, to Manuf. STD. | (8) (9) (11)
| 2 to 12 | 150 | Fig'd, RF | ASTM A-216 WCB Body, 18-8 SS Ball & Stem, PTFE Seals, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-Static Design, to API 609 | (6) (11)
| 14 to 16 | 150 | Fig'd, RF | ASTM A-216 WCB Body, Ball & Stem to be 18-8 SS, PTFE Seats, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-Static Design, Gear Operated, to Manuf. Std. | (6) (11)
Butterfly
| 2 to 20 | 150 | Lugged (through drilled) | Ductile Iron Body, Buna-N Lined, Aluminum Bronze Disc, Stainless Steel Shaft, Tight Shut-off, Wrench Operator to be capable of being positively locked in any position, to API 609 | (11)
Check
| 2 & over | 150 | Fig'd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6)
| 2 & under | 800 | Threaded | 13 CR Trim, ASTM A-105 Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check to Manuf. Std | (8)
Gate
| 2 & over | 150 | Fig'd, RF | 13 CR Trim, ASTM A-216 WCB Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (6) (7)
| 2 & under | 800 | Threaded | 13 CR Trim, ASTM A-105 Body, BB, OS&Y, BG, Solid Wedge, to API 602 | (7) (8)
Gauge
| 3/4 | 10 mPa @ 455 C (1500 psi @ 850 F) | Threaded or Socketweld Inlet | ASTM A-105, Normalised Body for Socketweld only, 316 SS Stem & Ball, Hard Seat, OS&Y Bonnet, Adhesion Packing, 3 x 1/2 FNPT Outlets, for Socketweld Body Hardness 187 HB Max. | (16) (17)
Caption: Table 4.1 Class UAW — Valve specifications for Air and Water service, ANSI Class 150
Extracted from 03-piping-materials-and-line-classes-01 page 26, table 1.