## table-4-2-class-uaz-fire-hydran
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
FIRE HYDRANT
| 125 | Flg'd, FF |  | 4-1/2" Seat Opening, 7-1/4" Barrel, Regular type, 6" Flanged Inlet, to Open Left, Painted with two coats of Red paint, four 2-1/2" Threaded Hose Nozzles, each Nozzle with Cap and Chain, Cap with CSA Stud Nut, Operating Nut to be CSA Standard Operating Nut, Darling B-50-B-M (Canada Valve and Hydrant Company), or approved equal | (2) (4) (5) (6) (7)
MONITOR HYDRANT
| 125 | Flg'd, FF |  | 4-1/2" Seat Opening, 7-1/4" Barrel, Regular type with 3", 125 PSI Flanged Elbow for mounting a Monitor Nozzle, 6" Flanged Inlet, to open Left, Painted with two Coats of Red Paint, three 2-1/2" Threaded Hose Nozzles, each Nozzle with Cap and Chain, Cap with CSA Standard Nut, Operating Nut to be CSA Standard Operating Nut, Nozzle Orientation (Clockwise) -0 Hose Connection, 90 and 180 Hose Connections, 270 Monitor Elbow, Darling B-50-B-M (Canada Valve and Hydrant Company) or approved equal | (2) (4) (5) (6) (7)
Caption: Table 4.2 Class UAZ — Fire Hydrant and Monitor Hydrant specifications
Extracted from 03-piping-materials-and-line-classes-01 page 29, table 1.