## table-4-3-line-class-sab
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched-80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1) (2)
| 3 to 10 | Sched-40 Min. | Seamless | ASTM A-53 GR.B or API-5L GR.B, Electric Furnace or Basic Oxygen ASTM A-106 GR.B also acceptable | (1)
| 12 to 24 | Std. Wt. Min. | Seamless | ASTM A-53 GR.B or API-5L GR.B, Electric Furnace or Basic Oxygen ASTM A-106 GR.B also acceptable | (1)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers etc.
| 2 & under | 3000# | Socketweld | ASTM A-105 Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless, Normalized | (3)
Nipples & Swages
| 1 1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (13) (14)
Unions
| 1 1/2 & under | 3000# | Socketweld | ASTM A-105 with Integral Seats, MSS SP-83, Heat Treated | (13)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (13) (15)
FLANGES
| 2 & 3 | 300 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (13) (15)
| 2 & under | 300 | SW, RF | ASTM A-105, Heat Treated | (5) (6) (13)
| 4 & over | 150 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (13)
BOLTING | Stud Bolts : ASTM A-193, GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Compressed Asbestos Composition 1/16" Thick
VALVES: Check
| 2 & 3 | 300 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6) (8) (9)
Caption: Table 4.3 Line Class SAB — Pipe, Fittings, Flanges, Bolting, Gaskets, Valves specifications
Extracted from 03-piping-materials-and-line-classes-01 page 31, table 1.