## table-4-6-class-paa
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1)(2)
| 3 to 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B or API 5L GR.B, Electric Furnace or Basic Oxygen, A-106 GR.B also acceptable | (1)
| 12 to 24 | Std. Wt. Min. | Seamless | ASTM A-53 GR.B or API 5L GR.B, Electric Furnace or Basic Oxygen, A-106 GR.B also acceptable | (1)
| 26 & over | Calculate | Electric Fusion Welded | API 5L GR.B, EF, or BO, or ASTM A-671 GR.CC60, Class 22
FITTINGS
Ells, Tees, Reducers, etc. |  |  |  |  | (1)
| 2 & under | 3000# | Threaded or Socketweld | ASTM A-105, Heat-treated Socketweld only | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2)(4)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (13)(14)
Threadolets
| 2 & under | 3000# | Threaded | ASTM A-105, Heat Treated | (13)
Unions
| 1-1/2 & under | 3000# | Socketweld or Threaded | ASTM A-105 with Integral Seats, MSS SP-83, Heat-treated Socketweld only | (13)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3)(13)(15)
FLANGES
| 2 & under | 150 | WN, RF | ASTM A-105, Heat Treated | (3)(6)
| 2 & under | 150 | SW, RF | ASTM A-105, Heat Treated | (13)(15)(5)(6)(13)
BOLTING | Stud Bolts: ASTM A-193, GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Compressed Asbestos Composition 1/16" Thick
Caption: TABLE: 4.6 CLASS: PAA
Extracted from 03-piping-materials-and-line-classes-01 page 40, table 1.