## table-4-6-paa-valves
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Ball
| 2 & over | 150 | Flg'd, RF | ASTM A-216 WCB Body, Ball and Stem to be either 18-8 SS or CS Nickel Plated Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS 5146, Anti-static Design, to API 608 | (6) (12) (18)
| 2 & under | 800 | Threaded or Socketweld | ASTM A-105, Heat-treated Body, Socketweld only, 18-8 SS Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS 5146, Anti-static Design, Socketweld Ends with a Swing-out Body or SW Ends Fitted with 150 mm (6") Long Plain End Nipples Welded in by Manuf. Pipe Nipples to be Seamless to ASTM A-106 GR.B, Sched. 160 Min., Wrench Operated, to Manuf. STD. | (10) (42) (13) (16)
Check
| 2 & over | 150 | Flg'd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (8) (8)
| 2 & under | 800 | Threaded or Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, Socketweld only, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (8) (10) (13)
Gate
| 2 & over | 150 | Flg'd, RF | 13 CR Trim, ASTM A-216 WCB Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (6) (8) (11)
| 2 & under | 800 | Threaded or Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, Socketweld only, W8, OS&Y, BG, Solid Wedge, to API 602 | (7) (8) (9) (10) (11) (13)
| 3/4 & under | 800 | Male SW/ Female Thrd | 13 CR Trim, ASTM A-105, Heat-treated Body, W8, OS&Y, BG, Solid Wedge, to API 606 | (7) (8) (13) (17)
Gauge
| 3/4 | 10 MPa @ 455 C (1500 psi @ 850 F) | Socketweld Inter | ASTM A-105, Normalized Body for Socketweld Only, 316 SS Stem & Ball, Hard Seat, OS&Y Bonnet, Asbestos Packing, 3 x 1/2 FNPT Outlet, for Socketweld Body Hardness 187 HB Max. | (18) (19)
Caption: Table 4.6 PAA — Valves specification table
Extracted from 03-piping-materials-and-line-classes-01 page 41, table 1.