## table-4-12-class-pae-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1) (2)
| 3 to 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B or API 5L GR.B, Electric Furnace or Basic Oxygen ASTM A-106 GR.B also acceptable | (1)
| 12 to 24 | Calculate Std. Wt. Min. | Seamless | ASTM A-53 GR.B or API 5L GR.B, Electric Furnace or Basic Oxygen ASTM A-106 GR.B also acceptable | (1)
| 26 & over | Calculate | Electric Fusion Welded | API 5L GR.B, EF or BO or ASTM A-671 GR.CC60, Class 22
FITTINGS
Ells, Tees, Reducers, etc. |  |  |  |  | (1)
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (12) (13)
Unions |  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (12) (14)
FLANGES
| 2 & over | 300 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (12) (14)
| 2 & under | 300 | SW, RF | ASTM A-105, Heat Treated | (8) (12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering ring
VALVES: Check
| 2 & over | 300 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6) (8) (16)
Caption: Table 4.12 Class PAE — Piping Materials and Line Class Specifications
Extracted from 03-piping-materials-and-line-classes-01 page 60, table 1.