## table-4-14-class-pag-sr
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (11)(2)
| 3 & 10 | Calculate Sched. 40 Min. | Seamless | ASTM A-106 GR.B or API-5L GR.B, Electric Furnace or Basic Oxygen | (1)
| 12 & 24 | Calculate Std. Wt. Min. | Seamless | ASTM A-106 GR.B or API-5L GR.B, Electric Furnace or Basic Oxygen | (1)
| 26 & over | Calculate | Electric Fusion Welded | ASTM A-671 GR.CC60, Class 22 | (14)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Sockerweld | ASTM A-105, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2)(4)
Sockolets
| 2 & under | 3000# | Sockerweld | ASTM A-105, Heat Treated | (12)(13)
Unions |  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3)(12)(14)
FLANGES
| 2 & over | 600 | WN, RF | ASTM A-105, Heat Treated | (3)(7)(12)(14)
| 2 & under | 600 | SW, RF | ASTM A-105, Heat Treated | (7)(12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7M with ASTM A-194 GR.2HM Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & over | 600 | Flgd, RF | 316 SS Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. & NACE MR-01-75 | (7)(9)
Caption: TABLE 4.14 CLASS: PAG (SR) — Pressure-Temperature Rating ANSI Class 600 Except 260°C (500°F) Max. (15)
Extracted from 03-piping-materials-and-line-classes-01 page 66, table 1.