## table-4-16-class-paj-piping-lin
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 160 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1)(2)
| 3 to 24 | Calculate | Seamless | ASTM A-106 GR.B, EF or BO | (13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 6000# | Socketweld | ASTM A-105, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB Seamless, Normalized | (3)
Nipple & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2)(4)
Socketolets
| 2 & under | 6000# | Socketweld | ASTM A-105, Heat Treated | (12)
Unions
|  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3)(6)(12)
FLANGES
| 2 & over | 1500 | WN, RF | ASTM A-105, Heat Treated | (3)(6)(7)(12)
| 2 & under | 1500 | SW, RF | ASTM A-105, Heat Treated | (7)(12)
BOLTING | Steel Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES: Check
| 2 & over | 1500 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB, Normalized Body, BC, Swing Check, to Manuf. STD. | (7)(9)
| 2 & under | 1500 | Socketweld | 13 CR Trim, ASTM A-105, Heat treated Body, BC, Horiz. or Vert. "Y" Pattern or Swing Check, to Manuf. STD. | (9)(10)(12)(14)
Gate
| 2 & over | 1500 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB, Normalized Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (7)(8)(9)(11)
Caption: Table 4.16 Class PAJ — Piping Line Class Specification
Extracted from 03-piping-materials-and-line-classes-01 page 72, table 1.