## table-4-16-class-paj-valve-spec
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Gate
| 2 & under | 1500 | Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, BB, OS&Y, BG, Solid Wedge, to API 602 | (8) (9) (10) (12) (14)
Gauge
| 3/4 | 10 MPa @ 455 C (1500 psi @ 850 F) | Socketweld Inlet | ASTM A-105, Normalized Body, 316 SS Stem & Ball, Hard Seat, OS&Y Bonnet, Asbestos Packing, 3 x 1/2 FNPT Outlets, Body Hardness 187 HB Max. | (14) (15) (16)
Globe
| 2 & over | 1500 | Flg'd, RF | 13 CR HFS Trim, ASTM A-216 WCB, Normalized Body, BB, OS&Y, BG1, Plug Disc, to Manuf. STD. | (7)
| 2 & under | 1500 | Socketweld | 13 CR HFS Trim, ASTM A-105, Heat-treated Body, BB, OS&Y, BG, Plug Disc, to Manuf. STD. | (10) (12) (14)
Caption: Table 4.16 CLASS: PAJ — Pressure-Temperature Rating, Service, Basic Material, Construction Class, Corrosion Allowance, and Valve Specifications
Extracted from 03-piping-materials-and-line-classes-01 page 73, table 1.