## table-4-19-class-pch-piping-lin
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-335 GR.P11, Heat Treated | (11)(2)(12)
| 3 to16 | Calculate | Seamless | ASTM A-335 GR.P11, Heat Treated | (12)
| 18 & over | Calculate | Electric Fusion Welded | ASTM A-691 GR. 1-1/4 CR, Class 22 Heat Treated | (12)
FITTINGS
Ells, Tees, Reducers, etc. |  |  |  |  | (1)
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F11, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WP11, Heat Treated | (3)(12)
Nipples & Swages
| 1-3/2 & under | See Notes | Seamless | ASTM A-335 GR.P11, Heat Treated | (2)(12)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F11, Heat Treated | (10)(12)
Unions
|  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F11, Heat Treated | (3)(11)(12)
FLANGES
| 2 & over | 900 | WN, RF | ASTM A-182 GR.F11, Heat Treated | (3)(5)(111)(12)
| 2 & under | 900 | SW, RF | ASTM A-182 GR.F11, Heat Treated | (5)(12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 455 C (850 F). ASTM A-193 GR.B16 with ASTM A-194 GR.3 Nuts, for service up to 645 C (1200 F) |  |  |  | (14)
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring, for service up to 455 C (850 F). Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 1/8" Thick 304 SS Centering Ring, above 455 C (850 F) |  |  |  | (15)
Caption: Table 4.19 Class PCH — Piping Line Class Specification
Footnote (1): Fittings note (1)
Footnote (2): Pipe/nipple note (2)
Footnote (3): Size / schedule note (3)
Footnote (4): Unions not allowed
Footnote (5): Flange note (5)
Footnote (10): Socketolet note (10)
Footnote (11): Schedule note (11)
Footnote (12): Heat treatment note (12)
Footnote (14): Bolting note (14)
Footnote (15): Gasket note (15)
Footnote (16): Material/temperature note (16)
Footnote (111): Flange note (111)
Extracted from 03-piping-materials-and-line-classes-01 page 80, table 1.