## table-4-23-class-peb
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-335 GR.P5, Heat Treated | (11)(2)(12)
| 3 to 16 | Calculate Sched. 40 Min. | Seamless | ASTM A-335 GR.P5, Heat Treated | (3)(12)
| 18 & over | Calculate | Electric Fusion Welded | ASTM A-691 GR.5 CR, Class 22 Heat Treated | (12)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc. | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F5, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WP5, Heat Treated | (3)(12)
Nipples & Swages | 1-1/2 & under | See Notes | Seamless | ASTM A-335 GR.P5, Heat Treated | (2)(12)
Sockolets | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F5, Heat Treated | (10)(32)
Unions |  |  |  | Not Allowed | (4)
Weldolets | 2 & over | See Notes | Buttweld | ASTM A-182 GR.F5, Heat Treated | (3)(11)(12)
FLANGES
| 2 & under | 300 | SW, RF | ASTM A-182 GR.F5, Heat Treated | (5)(12)
| 2 & 3 | 300 | WN, RF | ASTM A-182 GR.F5, Heat Treated | (3)(5)(12)
| 4 & over | 150 | WN, RF | ASTM A-182 GR.F5, Heat Treated | (5)(51)(12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 455 C (850 F). ASTM A-193 GR.B16 with ASTM A-194 GR.3 Nuts, for service up to 615 C (1200 F) |  |  |  | (14)
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring, for service up to 455 C (850 F). Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 1/8" Thick 304 SS Centering Ring, above 455 C (850 F) |  |  |  | (15)
Caption: Table 4.23 Class PEB — Pressure-Temperature Rating, Basic Material, Construction Class, Pipe, Fittings, Flanges, Bolting, Gaskets
Extracted from 03-piping-materials-and-line-classes-01 page 92, table 1.