## table-4-30-class-pjb
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Ball | 2 & 3 | 300 | Flgd, RF | 304 SS or 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS 5146, Anti-static Design, to API 608 | (5) (9)
| 2 & under | 150 | Socketweld | 304 SS or 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, Socketweld Ends with Swing-out Body or SW Ends Fitted with 150 mm (6") Long Plain End Nipples Welded in by Manuf. Pipe Needles to be Seamless to ASTM A-312 GR 304, Sched. 80S Min., Wrench Operated, to Manuf. STD. | (7) (9)
| 4 & over | 150 | Flgd, RF | 304 SS or 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blow out Stem, Secondary Steel Seats, Fire Tested to BS 5146, Anti-static Design, to API 608 | (5) (9)
Check | 2 & 3 | 300 | Flgd, RF | 304 SS Trim, ASTM A-351 GR CF8 or CF8M Body, BC, Swing Check, to Manuf. STD. | (5) (13)
| 2 & under | 800 | Socketweld | 304 SS Trim, ASTM A-182 GR F304 or F316 or A-351 GR CF8 or CF8M Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (7) (13)
| 4 & over | 150 | Flgd, RF | 304 SS Trim, ASTM A-351 GR CF8 or CF8M Body, BC, Swing Check, to Manuf. STD. | (5) (13)
Gate | 2 & 3 | 300 | Flgd, RF | 304 SS Trim ASTM A-351 GR CF8 or CF8M Body, OS&Y, BG, Solid Wedge, to API 600 | (5) (8) (13)
| 2 & under | 800 | Socketweld | 304 SS Trim, ASTM A-182 GR F304 or F316 or A-351 GR CF8 or CF8M Body, BB, OS&Y, BG, Solid Wedge, to API 602 | (6) (7) (8) (13) (14)
| 4 & over | 150 | Flgd, RF | 304 SS Trim ASTM A-351 GR CF8 or CF8M body, BB, OS&Y, BG, Solid Wedge, to API 600 | (5) (8) (13)
Caption: Table 4.30 CLASS: PJB — Pressure-Temperature Rating: ANSI Class 150 Except 340 C (650 F) Max. (15)
Extracted from 03-piping-materials-and-line-classes-01 page 114, table 1.