## table-4-34-class-pkb-valves
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Ball
| 2 & over | 300 | Flgd, RF | 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, to API 608 | (5) (9)
| 2 & under | 150 | Socketweld | 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, Socketweld Ends with Swing-out Body or SW Ends Fitted with 150 mm (6") Long Plain Nipples Welded in by Manuf. Pipe Nipples to be Seamless at ASTM A-312 GR 316, Sched 80S Min., Wrench Operated, to Manuf. STD. | (7) (9)
| 4 & over | 150 | Flgd | 316 SS Body, Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS 5146, Anti-static Design, to API 608 | (5) (9)
Check
| 2 & 3 | 300 | Flgd, RF | 316 SS Trim, A-351 GR CF8M Body, BC, Swing Check, to Manuf. STD. | (5) (13)
| 2 & under | 800 | Socketweld | 316 SS Trim, ASTM A-182 GR F316 or A-351 GR CF8M Body, BC, Horiz. or Ver. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (7) (13)
| 4 & over | 150 | Flgd, RF | 316 SS Trim, A-351 GR CF8M Body, BC, Swing Check, to Manuf. STD. | (5) (13)
Gate
| 2 & 3 | 300 | Flgd, RF | 316 SS Trim, A-351 GR CF8M Body, BB, OS&Y BG, Solid Wedge, to API 600 | (5) (8) (13)
| 2 & under | 800 | Socketweld | 316 SS Trim, ASTM A-182 GR F316 or A-351 GR CF8M Body, BB, OS&Y BG, Solid Wedge, to API 600 | (6) (7) (8) (13) (14)
| 4 & over | 150 | Flgd, RF | 316 SS Trim, A-351 GR CF8M Body, BB, OS&Y BG, Solid Wedge, to API 600 | (5) (8) (13)
Caption: Table 4.34 Class PKB — Pressure-Temperature Rating, Basic Material, Construction Class, Corrosion Allowance, Valves
Extracted from 03-piping-materials-and-line-classes-01 page 126, table 1.