## table-4-37-class-pkh-piping-com
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 1 1/2 & under | Calculate Sched. 40S Min. | Seamless | ASTM A-312 GR.TP316 | (1)(2)
| 12 & over | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1
| 2 to 10 | Calculate | Seamless | ASTM A-312 GR.TP316
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
| 3 & 10 | See Notes | Buttweld | ASTM A-403 GR.WP316, Seamless or GR.WP-WX316 EFW | (3)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WX316 EFW | (3)
Nipples & Swages |  |  |  |  | (2)
| 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.316
| 2 x 1-1/2 | Calculate | Seamless | ASTM A-312 GR.316
Socketolets
| 2 & under | 3000# |  | ASTM A-182 GR.F316
Unions |  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F904 | (3)(9)
FLANGES
| 2 & over | 900 | WN, RF | ASTM A-182 GR.F316 | (3)(5)(9)
| 2 & over | 900 | SW, RF | ASTM A-182 GR.F316 | (5)
BOLTING | Stud Bolts: ASTM A-193 GR.B7, with ASTM A-194 GR.2H Nuts, for service up to 175 C (350 F); ASTM A-193 GR.B8 Class 2 or B8A with ASTM A-194 GR.8 or 8A Nuts, for service up to 455 C (850 F) |  |  |  | (10)
GASKETS | Spiral Wound to API 601, 316 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
Caption: Table 4.37 Class PKH — Piping component specifications
Footnote (1): See notes
Footnote (2): See notes
Footnote (3): See notes
Footnote (4): Not Allowed
Footnote (5): See notes
Footnote (9): See notes
Footnote (10): See notes
Extracted from 03-piping-materials-and-line-classes-01 page 133, table 1.