## table-4-38-pkj-line-class
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| All | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1
FITTINGS
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
| 3 & 10 | See Notes | Buttweld | ASTM A-403 GR.WP316, Seamless or GR.WP.WX304 EFW | (2)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WP.WX304 EFW | (2)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.316 | (1)
| 2 x 1-1/2 | Calculate | Seamless | ASTM A-312 GR.316
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
Unions |  |  |  | Not Allowed | (3)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F316 | (2) (8)
FLANGES
| 2 & over | 1500 | WN, RF | ASTM A-182 GR.F316 | (2) (14) (8)
| 2 & under | 1500 | SW, RF | ASTM A-182 GR.F316 | (4)
BOLTING |  | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 175 C (350 F); ASTM A-193 GR.B8 Class 2 or BRA with ASTM A-194 GR.8 or 8A Nuts, for service up to 455 C (850 F) |  |  | (9)
GASKETS |  | Spiral Wound to API 601, 316 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & over | 1500 | Flg'd | 316 SS Trim, ASTM A-351 GR.CF8M Body, BC, Swing Check, to Manuf. STD. | (4) (10)
| 2 & under | 1500 | Socketweld | 316 SS Trim, ASTM A-182 GR.F316 or A-351 GR.CF8M Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (6) (10)
Caption: Table 4.38 PKJ Line Class — Pipe, Fittings, Flanges, Bolting, Gaskets, Valves
Extracted from 03-piping-materials-and-line-classes-01 page 136, table 1.