## table-4-40-class-prg-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE | 1-1/2 & under | Calculate Sched. 40S Min. | Seamless | ASTM A-312 GR.TP321H | (1)(2)
| 12 & over | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP321H or ASTM A-358 GR.321H, Class 1
| 2 to 10 | Calculate | Seamless | ASTM A-312 GR.TP321H
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc. | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F321H
| 3 & 10 | See Notes | Buttweld | ASTM A-403 GR.WP321H, Seamless or GR.WP.WX321H EFW | (3)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WP.WX321H EFW | (3)
Nipples & Swages | 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.321H | (2)
| 2 x 1-1/2 | Calculate | Seamless | ASTM A-312 GR.321H
Socketolets | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F321H
Unions |  |  |  | Not Allowed | (4)
Weldolets | 2 & over | See Notes | Buttweld | ASTM A-182 GR.F321H | (3)(9)
FLANGES | 2 & over | 600 | WN, RF | ASTM A-182 GR.F321H | (3)(5)(9)
| 2 & under | 600 | SW, RF | ASTM A-182 GR.F321H | (5)
BOLTING | Stud Bolts: ASTM A-193 GR.B8 Class 1 or B8T Class 1 with ASTM A-194 GR.8 or 8A Nuts, for service up to 595 C (1100 F); ASTM A-453 GR.660 Class A with ASTM A-194 GR.8 or 8A Nuts, for service up to 705 C (1300 F) |  |  |  | (12)
GASKETS | Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 1/8" Thick 304 SS Centering Ring
Caption: Table 4.40 Class PRG Piping Materials and Line Class Specification
Footnote (1): Referenced in FITTINGS section
Footnote (2): Referenced for Nipples & Swages
Footnote (3): See Notes
Footnote (4): Not Allowed (Unions)
Footnote (5): Referenced for Flanges
Footnote (9): Referenced for Weldolets and Flanges
Footnote (12): Referenced for Bolting
Extracted from 03-piping-materials-and-line-classes-01 page 141, table 1.