## table-4-43-class-rab
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | Seamless | ASTM A-333 GR 6 | (13)(2)
| 3 & 10 | Sched. 40 Min. | Seamless | ASTM A-333 GR 6 | (1)
| 12 to 14 | Std. Wt. Min. | Seamless | ASTM A-333 GR 6 | (1)
| 16 & over | Calculate | Electric Fusion Welded | Normalized CS to ASTM A-671 GR CC70 Class 22 (Supplement S-2 and S-3)
FITTINGS
Ells, Tees, Reducers, etc. |  |  |  |  | (1)
| 2 & under | 3000# | Socketweld | ASTM A-350 GR LF2, Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-420 GR WPL6, Seamless, Heat Treated | (13)(13)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-333 GR 6 | (2)
Sockolets
| 2 & under | 3000# | Socketweld | ASTM A-350 GR LF2, Heat Treated | (11)(13)
Unions
| 1-1/2 & under | 3000# | Socketweld | ASTM A-350 GR LF2, with Integral Seats, MSS SP-83, Heat Treated | (13)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-350 GR LF2, Heat Treated | (3)(12)(13)
FLANGES
| 2 & 3 | 300 | WN, RF | ASTM A-350 GR LF2, Heat Treated | (3)(5)(12)(13)
| 2 & under | 300 | SW, RF | ASTM A-350 GR LF2, Heat Treated | (4)(5)(13)
| 4 & over | 150 | WN, RF | ASTM A-350 GR LF2, Heat Treated | (3)(5)(13)
BOLTING | Stud Bolts: ASTM A-320 GR L7 with ASTM A-194 GR 7 Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & 3 | 300 | Flgd, RF | 13 CR Trim, ASTM A-352 GR LCB Body, BC, Swing Check, to Manuf. STD. | (5)(7)
Caption: TABLE 4.43 CLASS: RAB
Extracted from 03-piping-materials-and-line-classes-01 page 149, table 1.