## table-4-43-class-cadsr
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1) (2)
| 3 & 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 12 to 24 | Calculate Std. Wt. Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 1 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (12)
| 1-1/2 & over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketlets
| 1 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (8) (12)
Unions
| 1 & under | 3000# | Socketweld | ASTM A-105 with Integral Seats, MSS SP-83, Heat Treated | (12)
Weldolets
| 1-1/2 & under | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (9) (12) (15)
FLANGES
| 1 & under | 300 | SO, RF | ASTM A-105, Heat Treated | (5) (6) (12)
| 1-1/2 & over | 300 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (9) (12) (15)
BOLTING | Stud Bolts: ASTM A-193, GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Compressed Asbestos Composition 1/16" Thick
VALVES
Check
| 1 & under | 800 | Socketweld | Monel Trim, ASTM A-105, Heat-treated Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (10) (12) (13)
Caption: TABLE 4.43 CLASS: CAD(SR)
Extracted from 03-piping-materials-and-line-classes-01 page 164, table 1.