## table-4-49-class-hab-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE | 2 & under | Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1) (2)
| 3 & 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 12 & 24 | Std. Wt. Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 26 & over | Calculate | Electric Fusion Welded | API-5L GR.B, EF or BO, or ASTM A-671, GR.CC60, Class 22
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc. | 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (14)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages | 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketlets | 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (14) (15)
Unions |  |  |  | Not Allowed | (5)
Weldolets | 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (14) (16)
FLANGES | 2 & 3 | 300 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (14) (16)
| 2 & under | 300 | SW, RF | ASTM A-105, Heat Treated | (6) (14) (16)
| 4 & over | 150 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (14)
BOLTING | Steel Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
Caption: Table 4.49 CLASS HAB — Piping Materials and Line Class Specifications
Extracted from 03-piping-materials-and-line-classes-01 page 167, table 1.