## table-4-49-class-hab
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
VALVES
Ball
| 2 & 3 | 300 | Flgd, RF | ASTM A-216 WCB Body, Ball & Stem to be Either 18-8 SS or CS Nickel Plated, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, to API 608 | (6) (13)
| 2 & under | 800 | Socketweld | ASTM A-105, Heat-treated Body, 18-8 SS Ball & Stem, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, Socketweld Ends with Swing-out Body or SW Ends Fitted with 150 mm (6") Long Plain End Nipples Welded in by Manuf., Pipe Nipples to be Seamless to ASTM A-106 GR B, Sched. 160 Min, Wrench Operated, to Manuf. STD. | (10) (13) (14)
| 4 & over | 150 | Flgd, RF | ASTM A-216 WCB Body, Ball & Stem to be Either 18-8 SS or CS Nickel Plated, Reinforced PTFE Seats, Reinforced PTFE Stem Seal, Anti-blowout Stem, Secondary Steel Seats, Fire Tested to BS5146, Anti-static Design, to API 608 | (6) (11)
Check
| 2 & 3 | 300 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6) (8)
| 2 & under | 800 | Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (8) (10) (14)
| 4 & over | 150 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6) (8)
Gate
| 2 & 3 | 300 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (6) (8) (11)
| 2 & under | 800 | Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, WB, OS&Y, BG, Solid Wedge, to API 602 | (8) (9) (10) (14)
| 4 & over | 150 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (6) (8) (11)
Caption: Table 4.49 CLASS: HAB — Process-Hydrogen, Carbon Steel (12), ANSI Class 150 Except 205 C (400 F) Max. (12), Corrosion Allowance: 1.6 mm (0.063")
Extracted from 03-piping-materials-and-line-classes-01 page 168, table 1.