## table-4-50-had-pipe-fittings-fl
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1) (2)
| 3 & 10 | Sched. 40 Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 12 & 24 | Calculate Std. Wt. Min. | Seamless | ASTM A-53 GR.B, API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 26 & over | Calculate | Electric Fusion Welded | API-5L GR.B, EF or BO or ASTM A-671, GR.CC60, Class 22
FITTINGS
Ells, Tees, Reducers, etc. |  |  |  |  | (1)
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (14)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (14) (15)
Unions
|  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (14) (16)
FLANGES
| 2 & over | 300 | WN, RF | ASTM A-105, Heat Treated | (3) (6) (16)
| 2 & under | 300 | SW, RF | ASTM A-105, Heat Treated | (8) (14) (16)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
Caption: Table 4.50 HAD — Pipe, Fittings, Flanges, Bolting, and Gaskets specification table
Extracted from 03-piping-materials-and-line-classes-01 page 171, table 1.