## table-4-51-hag-piping-specifica
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (1)(2)
| 3 & 10 | Calculate | Seamless | ASTM A-53 GR.B, or API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)
| 12 & 24 | Calculate | Seamless | ASTM A-53 GR.B or API-5L GR.B, Electric Furnace or Basic Oxygen, ASTM A-106 GR.B also acceptable | (1)(14)
| 26 & over | Calculate | Seamless | ASTM A-671 GR CC60, Class 22 | (14)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2)(4)
Sockolets
| 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (13)(15)
Unions |  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3)(13)(16)
FLANGES
| 2 & over | 600 | WN, RF | ASTM A-105, Heat Treated | (3)(6)(13)(16)
| 2 & under | 600 | SW, RF | ASTM A-105, Heat Treated | (8)(13)(16)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & over | 600 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6)(8)
Caption: Table 4.51 HAG Piping Specification — Pipe, Fittings, Flanges, Bolting, Gaskets, Valves
Extracted from 03-piping-materials-and-line-classes-01 page 174, table 1.