## table-4-52-class-hah-specificat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 3 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (11)(2)
| 4 to 24 | Calculate Sched. 120 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (13)(13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc. | 2 & under | 3000# | Socketweld | ASTM A-105, Heat Treated | (12)
| 3& over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages | 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2)(4)
Socketolets | 2 & under | 3000# |  | ASTM A-105, Heat Treated | (12)(14)
Unions |  |  |  | Not Allowed | (5)
Weldolets | 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3)(11)(12)(15)
FLANGES | 2 & over | 900 | WN; RF | ASTM A-105, Heat Treated | (3)(6)(12)(15)
| 2 & under | 900 | SW, RF | ASTM A-105, Heat Treated | (6)(12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 3/8" Thick Carbon Steel Centering Ring
VALVES
Check | 2 & over | 900 | Flg'd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6)(8)
| 2 & under | 1500 | Socketweld | 13 CR Trim, ASTM A-105, Heat-treated Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (8)(9)(12)(16)
Caption: Table 4.52 Class HAH — Pressure-Temperature Rating, Materials, and Component Specifications
Extracted from 03-piping-materials-and-line-classes-01 page 177, table 1.