## table-4-53-class-haj-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 3 & under | Calculate Sched. 160 Min. | Seamless | ASTM A-106 GR.B, EF or BO | (11) (2)
| 4 to 24 | Calculate | Seamless | ASTM A-106 GR.B, EF or BO | (13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 6000# | Socketweld | ASTM A-105, Heat Treated | (12)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-106 GR.B | (2) (4)
Socketolets
| 2 & under | 6000# |  | ASTM A-105, Heat Treated | (12)
Unions |  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-105, Heat Treated | (3) (12) (14)
FLANGES
| 2 & over | 1500 | WN, RF | ASTM A-105, Heat Treated | (12) (13) (14)
| 2 & under | 1500 | SW, RF | ASTM A-105, Heat Treated | (6) (12)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & over | 1500 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BC, Swing Check, to Manuf. STD. | (6) (8)
| 2 & over | 1500 | Socketweld | 13 CR Trim, ASTM A-105, Heat treated Body, BC, Horiz. or Vert. "Y" Pattern Piston or Swing Check, to Manuf. STD. | (8) (9) (12) (15)
Gate
| 2 & over | 1500 | Flgd, RF | 13 CR Trim, ASTM A-216 WCB Body, BB, OS&Y, BG, Solid Wedge, to API 600 | (6) (7) (8) (10)
Caption: Table 4.53 Class HAJ — Piping Materials and Line Class Specification
Extracted from 03-piping-materials-and-line-classes-01 page 180, table 1.