## table-4-60-class-hee-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-335 GR.P5, Heat Treated | (11) (2) (13)
| 3 & 16 | Calculate Sched. 40 Min. | Seamless | ASTM A-335 GR.P5, Heat Treated | (3) (13)
| 18 & over | Calculate | Electric Fusion Welded | ASTM A-691, GR.5 CR, Class 22, Heat Treated (Supplement S3) | (13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F5, Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WP5, Heat Treated | (3) (13)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-335 GR.P5, Heat Treated | (2) (13)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F5, Heat Treated | (11) (13)
Unions |  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F5, Heat Treated | (3) (12) (13)
FLANGES
| 2 & over | 300 | WN, RF | ASTM A-182 GR.F5, Heat Treated | (3) (5) (12) (13)
| 2 & over | 300 | SW, RF | ASTM A-182 GR.F5, Heat Treated | (5) (13)
BOLTING |  |  | Steel Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 455 C (850 F); ASTM A-193 GR.B16 with ASTM A-194 GR.3 Nuts, for service up to 645 C (1200 F) |  | (14)
GASKETS |  |  | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring, for service up to 455 C (850 F); Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 1/8" Thick 304 SS Centering Ring, above 455 C (850 F) |  | (15)
Caption: Table 4.60 Class HEE piping materials and line class specification
Footnote (1): Fittings note
Footnote (2): Pipe size note
Footnote (3): Size note
Footnote (4): Unions not allowed
Footnote (5): Flanges note
Footnote (10): Material/rating note
Footnote (11): Pipe/fitting note
Footnote (12): Weldolet/flange note
Footnote (13): Heat treatment note
Footnote (14): Bolting note
Footnote (15): Gaskets note
Footnote (17): Rating note
Extracted from 03-piping-materials-and-line-classes-01 page 201, table 1.