## table-4-64-hfe-line-class-pipin
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-335 GR.P9, Heat Treated | (11) (2) (13)
| 3 & 16 | Calculate Sched. 40 Min. | Seamless | ASTM A-335 GR.P9, Heat Treated | (13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.P9, Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WP9, Heat Treated | (3) (13)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-335 GR.P9, Heat Treated | (2) (13)
Sockolets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.P9, Heat Treated | (11) (13)
Unions |  |  |  | Not Allowed. | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.P9, Heat Treated | (3) (12) (13)
FLANGES
| 2 & over | 300 | WN; RF | ASTM A-182 GR.P9, Heat Treated | (3) (5) (12) (13)
BOLTING
| 2 & under | 300 | SW; RF | ASTM A-182 GR.P9, Heat Treated | (5) (13)
Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 455 C (850 F). ASTM A-193 GR.B16 with ASTM A-194 GR.3 Nuts, for service up to 645 C (1200 F). |  |  |  |  | (14)
GASKETS
Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring, for service up to 455 C (850 F). Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 3/8" Thick 304 SS Centering Ring, above 455 C (850 F). |  |  |  |  | (15)
VALVES
Check
| 2 & over | 300 | Flg'd; RF | 13 CR Trim, ASTM A-217 GR.C12 Body; BC, Swing Check, to Manf. STD. | (5) (7)
Caption: Table 4.64 HFE Line Class — Piping Components
Extracted from 03-piping-materials-and-line-classes-01 page 213, table 1.