## table-4-63-class-hfg-piping-lin
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASTM A-335 GR.P9, Heat Treated | (11) (2) (13)
| 3 & 16 | Calculate | Seamless | ASTM A-335 GR.P9, Heat Treated | (13)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F9, Heat Treated | (13)
| 3 & over | See Notes | Buttweld | ASTM A-234 GR.WP9, Heat Treated | (3) (13)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-335 GR.P9, Heat Treated | (2) (13)
Socketolets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F9, Heat Treated | (11) (13)
Unions |  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F9, Heat Treated | (3) (12) (13)
FLANGES
| 2 & over | 600 | WN, RF | ASTM A-182 GR.F9, Heat Treated | (12) (13)
| 2 & under | 600 | SW, RF | ASTM A-182 GR.F9, Heat Treated | (5) (13)
BOLTING |  |  |  | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 455 C (850 F); ASTM A-193 GR.B16 with ASTM A-194 GR.3 Nuts, for service up to 645 C (1200 F) | (14)
GASKETS |  |  |  | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring, for service up to 455 C (850 F); Spiral Wound to API 601, 347 SS, Flexible Graphite Filler, with 3/8" Thick 304 SS Centering Ring, above 455 C (850 F) | (15)
VALVES
Check
| 2 & over | 600 | Figd, RF | 13 CR Trim, ASTM A-217 GR C12 Body, BC, Swing Check, to Manuf. STD. | (5) (7)
Caption: TABLE: 4.63 CLASS: HFG — Piping line class specification
Extracted from 03-piping-materials-and-line-classes-01 page 216, table 1.