## table-4-67-class-hje-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 1-1/2 & under | Schedule 40S Min. | Seamless | ASTM A-312 GR.TP304 | (1)(2)
| 12 & over | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP304 or ASTM A-358 GR.304, Class 1
| 2 to 10 | Calculate Sched. 10S Min. | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP304 or ASTM A-358 GR.304, Class 1 | (3)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F304
| 3 & 10 | See Notes | Buttweld | ASTM A-403 GR.WP304, Seamless or GR.WP-WX304 EFW | (3)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WP-WX304 EFW | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.304 | (2)
| 2 x 1-1/2 | Sched. 40S Min. | Seamless | ASTM A-312 GR.304 | (1)
Socketlets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F304
Unions |  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F304 | (3)(11)
FLANGES
| 2 & over | 300 | WN, RF | ASTM A-182 GR.F304 | (3)(5)(11)
| 2 & under | 300 | SW, RF | ASTM A-182 GR.F304 | (5)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 175 C (350 F); ASTM A-193 GR.B8, Class 2 or B8A with ASTM A-194 GR.8 or 8A Nuts, for service up to 455 C (850 F) |  |  |  | (10)
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
Caption: Table 4.67 CLASS HJE — Piping materials specification table
Extracted from 03-piping-materials-and-line-classes-01 page 222, table 1.