## table-4-69-hkb-line-class
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 to 10 | Calculate Sched. 10S Min. | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1 | (1)
| 1-1/2 & under | Sched. 40S Min. | Seamless | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1 | (1) (2)
| 12 & over | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
| 3 & 10 | See Notes | Buttweld | ASTM A-403 GR.WP316, Seamless or GR.WP-WX316 EFW | (3)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WP-WX316 EFW | (3)
Nipples & Swages
| 2 x 1-1/2 | Sched. 40S Min. | Seamless | ASTM A-312 GR.316 | (1)
| 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.316 | (2)
Socketlets
| 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
Unions
|  |  |  | Not Allowed | (4)
Weldolets
| 2 & over | See Notes | Buttweld | ASTM A-182 GR.F316 | (3) (11)
FLANGES
| 2 & 3 | 300 | WN, RF | ASTM A-182 GR.F316 | (13) (5) (11)
| 2 & under | 300 | SW, RF | ASTM A-182 GR.F316 | (5)
| 4 & over | 150 | WN, RF | ASTM A-182 GR.F316 | (3) (5)
BOLTING |  |  |  | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 175 C (350 F), ASTM A-193 GR.B8 Class 2 or B8A with ASTM A-194 GR.8 or 8A Nuts, for service up to 340 C (650 F) | (10)
GASKETS |  |  |  | Spiral Wound to API 601, 316 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
Caption: Table 4.69 HKB Line Class — Pipe, Fittings, Flanges, Bolting, Gaskets
Extracted from 03-piping-materials-and-line-classes-01 page 228, table 1.