## table-4-71-class-hkg-piping-mat
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE | 2 to 10 | Calculate | Seamless | ASTM A-312 GR.TP316
| 1-1/2 & under | Sched. 40S Min. | Seamless | ASTM A-312 GR.TP316 | (1) (2)
| 12 & over | Calculate | Seamless or Electric Fusion Welded | ASTM A-312 GR.TP316 or ASTM A-358 GR.316, Class 1
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc. | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
| 3 to 10 | See Notes | Buttweld | ASTM A-403 GR.WP316, Seamless or GR.WP-WX316 EFW | (3)
| 12 & over | See Notes | Buttweld | ASTM A-403 GR.WP-WX316 EFW | (3)
Nipples & Swages | 2 x 1-1/2 | Calculate | Seamless | ASTM A-312 GR.316
| 1-1/2 & under | See Notes | Seamless | ASTM A-312 GR.316 | (2)
Socketlets | 2 & under | 3000# | Socketweld | ASTM A-182 GR.F316
Unions |  |  |  | Not Allowed | (4)
Weldolets | 2 & over | See Notes | Buttweld | ASTM A-182 GR.F316 | (3) (10)
FLANGES | 2 & over | 600 | WN, RF | ASTM A-182 GR.F316 | (3) (5) (10)
| 2 & under | 600 | SW, RF | ASTM A-182 GR.F316 | (5)
BOLTING | Stud Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts, for service up to 175 C (350 F); ASTM A-193 GR.B8 Class 2 or B8A with ASTM A-194 GR.8 or 8A Nuts, for service up to 455 C (850 F). |  |  |  | (11)
GASKETS | Spiral Wound to API 601, 316 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES: Check | 2 & over | 600 | Flg'd | 316 SS Trim, ASTM A-351 GR.CF8M Body, BC, Swing Check, to Manuf. STD. | (5) (9) (12)
Caption: Table 4.71 Class HKG — Piping Materials Specification
Extracted from 03-piping-materials-and-line-classes-01 page 234, table 1.