## table-4-83-line-class-zag-pipin
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 & under | Calculate Sched. 80 Min. | Seamless | ASME SA-106 GR.B, EF or BO | (11)(2)
| 3 to 10 | Calculate Sched. 40 Min. | Seamless | ASME SA-53 GR.B or ASME SA-106 GR.B, EF, or BO | (1)
| 12 & 24 | Calculate STD. Wt. Min. | Seamless | ASME SA-53 GR.B or ASME SA-106 GR.B, EF or BO | (1)
FITTINGS |  |  |  |  | (1)
Ells, Tees, Reducers, etc.
| 2 & under | 3000# | Socketweld | ASME SA-105, Heat Treated | (14)
| 3 & over | See Notes | Buttweld | ASME SA-234 GR.WPB, Seamless, Normalized | (3)
Nipples & Swages
| 1-1/2 & under | See Notes | Seamless | ASME SA-106 GR.B | (2)(4)
Socketolets
| 2 & under | 3000# | Socketweld | ASME SA-105, Heat Treated | (13)(14)
Unions |  |  |  | Not Allowed | (5)
Weldolets
| 2 & over | See Notes | Buttweld | ASME SA-105, Heat Treated | (3)(14)(15)
FLANGES
| 2 & over | 600 | WN, RF | ASME SA-105, Heat Treated | (3)(7); (14)(15)
| 2 & under | 600 | SW, RF | ASME SA-105, Heat Treated | (7)(14)
BOLTING | Steel Bolts: ASTM A-193 GR.B7 with ASTM A-194 GR.2H Nuts
GASKETS | Spiral Wound to API 601, 304 SS, Asbestos Filler, with 1/8" Thick Carbon Steel Centering Ring
VALVES
Check
| 2 & over | 600 | Fig.d, RF or Buttweld | 13 CR Trim, ASME SA-216 WCB Heat-treated Body, RC, Swing Check, to Manuf. STD. | (6)(7)(9)
Caption: Table 4.83 Line Class ZAG — Piping materials and specifications
Extracted from 03-piping-materials-and-line-classes-01 page 265, table 1.