## table-4-84-pqb-piping-line-clas
ITEM | SIZE | RATING | TYPE | SPECIFICATIONS | NOTES
PIPE
| 2 to 10 | Sched. 40 | Seamless | Aluminum ASTM A345-6061-T6
| 1-1/2 & under | Sched. 160 | Seamless | Aluminum ASTM B345-6061-T6
FITTINGS Ells, Tees, Reducers, Couplings etc.
| 1-1/2 & under | 3000# | Sockerweld | Aluminum ASTM B361-WP6061-T6
Ells, Tees, Reducers, Couplings, etc.
| 2 & over | Sched. 40 | Buttweld | Aluminum ASTM B361-WP6061-T6
Nipples
| 1-1/2 & under | XXS | Sockerweld | Aluminum ASTM B361-WP6061-T6
Socketlets
| 2 & under | 3000# | Sockerweld | Aluminum ASTM B361-WP6061-T6
Weldolets
| 2 & over | Sched. 40 | Buttweld | Aluminum ASTM B361-WP6061-T6
FLANGES
| 2 & over | 150 | WN, RF | Aluminum ASTM B361-WP6061-T6 or ASTM B247-WP6061-T6 | (4) (7)
BOLTING | Stud Bolts: ASTM A-193 GR B5 Class 1 with ASTM A-194 GR.8M Nuts, Backing Washers 304 SS
GASKETS | Compresses Asbestos 1/16" Thick
VALVES Ball
| 2 to 4 | 150 | Flanged | Jamesbury A150F-44-36-TT, 316 SS Ball & Stem | (4)
| 6 to 10 | 150 | Flanged | Jamesbury D150F-44-36-TT, 316 SS Ball & Stem | (4)
| 1-1/2 & under | 300 | Threaded | Jamesbury A44-36-TT, 316 SS Ball & Stem | (5) (6)
Check
| 2 & over | 150 | Flanged | Aluminum-Mission Duo Check Fig.15 ASF
Caption: Table 4.84 PQB — Piping line class specification for Sour Gas and Sour Water Containing H2S, Aluminum, ANSI Class 150
Extracted from 03-piping-materials-and-line-classes-01 page 268, table 1.