## piping-class-a0-material-line-c
CODE B31.3 | CLASS A0
Service | Sweet Gas and Hydrocarbon Liquids, Glycol, Fuel Gas, Propane, Refrigerant, BFW (Note 20), Steam, Steam Cond., Pressure Relief, H.C. Drains, Lube Oil (Pickled.), Fire Water Per ANSI B16.5 Class 150 Material Group 1.1
Temperature Range | -29°C to 204°C
Maximum Corrosion Allowance | 0 mm
Radiography | 5% (Note 4)
Post Weld Heat Treatment | Per B31.3
ITEM | Sizes (NPS) | General Description | Material Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless : PE | A106 GR. B
| 2 - 10 | Seamless : BE | A106 GR. B
| 12 - 18 | Seamless | A106 GR. B | 18
| 20 - 24 | Seamless | A106 GR. B | 18
Fittings | 1/2 - 1 1/2 | Class 3000 SW/THD | A105N | 16
| 2 - 24 | Butt Weld, WT to match pipe | A234 WPB
Nipples | 1/2 - 1 1/2 | Seamless SCH160 TE/PE | A106 GR. B
Swages | 1/2 - 2 | Bore to match pipe | A234 WPB
Flanges | 1/2 - 1 1/2 | Class 150 RF THD/SW | A105N | 24
| 2 - 10 | Class 150 RFWN, bore to match pipe | A105N | 2, 31
| 12 - 24 | Class 150 RFWN, bore to match pipe | A105N | 2, 28, 31
Bolting | All | Studs | A193 GR. B7
|  | Nuts | A194 GR. 2H
Gaskets | All | Class 150 – 3 mm (1/8")THK "Flexitallic" Style CG, ASME B16.20 or Owner approved equivalent | 316 SS | 26
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-806/807/808, GA-100/101
| 3/4 - 6, 8 - 24 | Class 150 Flanged | GA-100/101
GLOBE
| 3/4 - 1 1/2 | Class 800 THD/SW | GL-806/807/808, GL-100
| 2 - 4 | Class 150 Flanged | GL-100
CHECK
| 3/4 - 1 1/2 | Class 800 THD/SW | CH-806/807/808/809
| 2 - 24 | Class 150 Flanged, Swing Type | CH-100
| 2 - 24 | Class 150 Flanged, Piston Type | CH-102
| 3/4 - 1 1/2 | Class 150 Wafer Type | CH-10X
BALL
| 3/4 - 1 1/2 | Class 600 THD- | BA-608 | 5
| 2 – 6, 8 - 10 | Class 150 Flanged | BA-100-101 | 5
BUTTERFLY
| 2 – 6, 8 - 12 | Class 150 | BU-100/101
Size | 1/2 | 3/4 | 1 | 1 1/2 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
W.T. | 160 | 160 | 160 | 160 | 160 | 40/std | 40/std | 40/std | 40/std | 40/std | 20 | 10 | 10 | 10 | 10 | 10 | 10
Caption: PIPING CLASS A0 — Piping Material Line Class Detail
Footnote 2: Maximum Spectacle Blind size shall be 12NPS. A blind and spacer shall be used for larger pipe sizes. Spectacle Blind material shall be A516 Gr 70N. For low temperature service, material shall be Charpy Y-notch tested at temperatures no warmer than the minimum allowable operating temperature.
Footnote 4: See Owner's Specification GS 2.10 for Nondestructive Examination requirements. When the amount of radiographic examination is less than 100%, the progressive examination requirements of B31.3 Clause 341.3.4 or CSA Z662 Clause 7.10.3.1 shall apply.
Footnote 5: Maximum allowable temperature 100°C.
Footnote 16: For glycol and hot oil service, use SW fittings, except valves which may be threaded.
Footnote 18: A53 Gr. B Pipe may be substituted with approval. (ERW for NPS 12-18, DSAW for NPS 20-24). Check wall thickness.
Footnote 24: If using SW flanges, bore to match pipe.
Footnote 26: For FF Flanges use Class 150 - 3 mm THK Full Face Gaskets, "Klinger® 1000", "Durlon-8600" or "Garlock 3150".
Footnote 28: RFSO flanges may be substituted with approval.
Footnote 29: For treated de-ironized boiler feed water upstream of the deaerator, use 304L stainless steel pipe and fittings with 316 stainless steel valves.
Footnote 31: Use Flat Faced (FF) flanges in firewater service or when mating to cast iron flanges.
Extracted from 03-piping-materials-and-line-classes-04 page 1, table 1.