## class-a1c-item-sizes-descriptio
ITEM | Sizes (NPS) | General Description | Material Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, PE | A333 GR. 6 | 1, 7
| 2 – 24 | Seamless, BE | A333 GR. 6 | 1, 7
Fittings | 1/2 – 1 1/2 | Class 3000 THD/SW | A350 LF 2 CL1 | 1, 7
| 2 – 24 | Butt Weld, WT to match pipe | A420 WPL 6 | 1, 7
Nipples | 1/2 – 1 1/2 | Seamless SCH 160 TE/PE | A333 GR. 6 | 1, 7
Flanges | 1/2 – 2 | Bore to match pipe | A350 WPL 6 | 1, 2
| 1/2 – 1 1/2 | Class 150 RF THD/SW | A350 LF 2 CL1 | 1, 7, 24
| 3/4 – 24 | Class 150 RFWN, bore to match pipe | A350 LF 2 CL1 | 1, 2
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM
Gaskets | All | Class 150: 3 mm (1/8") THK. "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent. | 316 SS | 8
Valves | GATE
| 1/2 – 1 1/2 | Class 800 THD/SW | GA-846/847/848 | 7
| 1/2 – 1 1/2 | Class 150 Flanged | GA-140 | 10
| 2 – 24 | Class 150 Flanged | GA-140/141
GLOBE
| 3/4 – 1 1/2 | Class 800 THD/SW | GL-846/847/848 | 7
| 2 – 4 | Class 150 Flanged | GL-140
CHECK
| 3/4 – 1 1/2 | Class 800 THD Flanged Swing type | CH-846/847/848/849 | 7
| 2 – 18 | Class 150 Flanged Swing type | CH-740
|  | Class 150 Wafer type | CH-14X
BALL
| 1/2 – 1 1/2 | Class 600 THD | BA-648 | 5, 7
| 2 – 6/8 – 10 | Class 150 Flanged | BA-140/141 | 5
Caption: CLASS A1C — Item, Sizes, General Description, Material Code, Notes
Extracted from 03-piping-materials-and-line-classes-04 page 3, table 2.