## class-a4-piping-component-speci
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, BE | A106 GR. B | 1, 2
| 2 – 24 | Seamless, BE | A106 GR. B | 1, 18
Fittings | 1/2 – 1 1/2 | Class 3000 THD/SW | A105 | 1, 7
| 2 – 24 | Butt Weld, WF, to match pipe | A234 WPB | 1
Nipples | 1/2 – 1 1/2 | Seamless SCH 160 TE/PE | A106 GR. B | 1, 7
Flanges | 1/2 – 2 | Bore to match pipe | A105 WN/FB | 1
| 1/2 – 1 1/2 | Class 150 RF/SW-THD | A105 | 1, 24
| 2 – 24 | Class 150 RFWN, bore to match pipe | A105 | 1, 2
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 150: 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent
Valves | GATE
| 1/2 – 1 1/2 | Class 800 SW/THD | GA-826/827/828 | 7
| 2 – 5, 8 – 24 | Class 150 Flanged | GA-120/121
GLOBE
| 3/4 – 1 1/2 | Class 800 SW/THD | GL-826/827/828 | 7
| 2 – 4 | Class 150 Flanged | GL-120
CHECK
| 3/4 – 1 1/2 | Class 800 SW/THD | CH-826/827/828 | 7
| 2 – 24 | Class 150 Flanged Swing type | CH-120
| 2 – 24 | Class 150 Wafer type | CH-525
BALL
| 1/2 – 1 1/2 | Class 800 THD | BA-826 | 5, 7
| 2 – 6, 8 – 24 | Class 150 Flanged | BA-120/121 | 5
Size | 1/2 | 3/4 | 1 | 1 1/2 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24
W.T. | 160 | 160 | 160 | 160 | 40/std | 40/std | 40/std | 40/std | 40/std | 20 | 20 | 10 | 10 | 10 | 10 | 20/std
Caption: CLASS A4 — Piping Component Specifications
Extracted from 03-piping-materials-and-line-classes-04 page 7, table 2.