## piping-class-a5g-material-speci
CODE CSA Z662 | CLASS A5G
Service | Sour Gas - (Pipelines, CSA Z662, Surface Piping)
Maximum Pressure Rating | Lower of ANSI B16.5 Class 150 Material Group 1.1 or CSA Z245.12 PN 20
Temperature Range | -45°C to 120°C
Minimum Corrosion Allowance | 3.0 mm
Radiography | 100%
Post Weld Heat Treatment | All Welds (Note 11)
Caption: Piping Class A5G — Material Specifications
Extracted from 03-piping-materials-and-line-classes-04 page 9, table 1.