## class-a7a-component-table
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, BE | A333 GR. 6
| 2 – 10 | Seamless, BE | A333 GR. 6
| 12 – 24 | Seamless, BE | A333 GR. 6
Fittings | 1/2 – 1 1/2 | 3000# THD/SW | A350 LF 2 CL1
| 2 – 24 | Butt Weld to match pipe | A420 WPL 6
Nipples | 1/2 – 2 | Seamless, SCH 160 TE/PE | A333 GR. 6
Swages | 1/2 – 2 | Bore to match pipe | A420 WPL 6
Flanges | 1/2 – 1 1/2 | Class 150 RF THD/SW | A350 LF 2 CL1
| 2 – 24 | Class 150 RF/WN, bore to match pipe | A350 LF 2 CL1 | 2
Bolting | All | Studs | A193 GR. B7M
|  | Nuts | A194 GR. 2HM
Gaskets | All | Class 150 - 3 mm (1/8") THK 'Flexitallic' Style CG | 316 SS
ASME B16.20 or Owner approved equivalent
Valves | GATE
| 1/2 – 1 1/2 | Class 800 THD/SW | GA-836/837/838
| 2 – 24 | Class 150 Flanged | GA-130/131
GLOBE
| 3/4 – 1 1/2 | Class 800 THD/SW | GL-836/837/838
| 2 – 4 | Class 150 Flanged | GL-130
CHECK
| 3/4 – 1 1/2 | Class 800 THD Lift type | CH-836/837/838/839
| 2 – 24 | Class 150 Flanged Swing type | CH-130
| 4 – 24 | Class 150 Wafer type | CH-13X
BALL
| 3/4 – 1 1/2 | Class 600 THD | BA-638 | 5
| 2 – 24 | Class 150 Flanged | BA-130/131 | 3
Caption: CLASS A7A — Component sizes, general descriptions, material codes, and notes
Extracted from 03-piping-materials-and-line-classes-04 page 11, table 2.