## piping-class-a7b-item-detail
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A333 GR. 3
| 2 - 24 | Seamless, BE | A333 GR. 3
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | A350 LF 3
| 2 - 24 | Butt Welded, WT to match pipe | A420 WPL 3
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 TE/PE | A333 GR. 3
Swages | 1/2 - 2 | Bore to match pipe | A420 WPL 3
Flanges | 1/2 - 1 1/2 | Class 150 RF THD/SW | A350 LF 3 | 24
| 2 - 24 | Class 150 RFWN, bore to match pipe | A350 LF 3 | 5
Bolting | All | Studs | A320 GR. L7
|  | Nuts | A194 GR. 4
Gaskets | All | Class 150 -3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-876/877/878
| 2 - 24 | Class 150 Flanged | GA-170/171
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL-876/877/878
| 2 - 4 | Class 150 Flanged | GL-170
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-876/877/878/879
| 2 - 24 | Class 150 Flanged Swing type | CH-170
| 2 - 24 | Class 150 Wafer type | CH-172
BALL
| 1/2 - 1 1/2 | Class 800 THD | BA-678 | 5
| 2 - 24 | Class 150 Flanged | BA-170/171 | 5
Caption: Piping Class A7B — Item Detail
Extracted from 03-piping-materials-and-line-classes-04 page 12, table 2.