## piping-class-a8-service-conditi
CODE B31.3 | CLASS A8
Service | Utility Water, Utility Air
Maximum Pressure Rating | Per ANSI B16.5 Class 150 Material Group 1.1 (Note 23)
Temperature Range | -29°C to 148°C
Minimum Corrosion Allowance | 0 mm
Radiography | 0% (Note 4)
Post Weld Heat Treatment | Per B31.3
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 2 | Seamless, ERW | A106 GR. B | 18, 39
| 2 - 10 | Seamless, BE | A106 GR. B | 18, 39
Fittings | 1/2 - 1 | Class 3000 TBE | A105
| 2 - 10 | Seamless WT, SCH 40 | A234 WPB
Nipples | 1/2 - 2 | Seamless SCH 160 TE | A106 GR. B | 18
Flanges | 1/2 - 2 | SCH 80 | A234 WPB
Flanges | 1/2 - 2 |  | A105N
| 2 - 10 | Class 150 RF | A105N
Bolting | All | Class 150 RFWN, SCH 40 | A105N
|  | Studs | A193-GR. B7
|  | Nuts | A194-GR. 2H
Gaskets | All | Class 150 ~3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 2 | Class 800 THD | GA-808
| 2 - 6, 8 - 10 | Class 150 Flanged | GA-100/101
GLOBE
| 3/4 - 2 | Class 800 THD | GL-808
| 2 - 4 | Class 150 Flanged | GL-100
CHECK
| 3/4 - 2 | Class 800 LR type | CH-808
| 2 - 10 | Class 150 Flanged Swing type | CH-100
| 2 - 10 | Class 150 Wafer type | CL-100
BALL
| 3/4 - 2 | Class 600 THD | BA-608 | 5
| 2 - 10 | Class 150 Flanged | BA-100 | 5
Caption: Piping Class A8 — service conditions and component schedule
Extracted from 03-piping-materials-and-line-classes-04 page 14, table 1.